## Slide 1: City of Santa Barbara Best Practices
Renewable Energy and Energy Conservation Lessons Learned
Jim Dewey – Facilities and Energy Manager
Central Coast Sustainability Summit 2014

## Slide 2: Best Practices and Lessons Learned
Developing Energy Projects
Sunk Cost vs. Personal Incentive
Learning to Work with the Utilities

## Slide 3: Developing Energy Projects
Chart: 
| Plug and Process Load | Mechanical Load | Lighting
Energy Use Categories | 0.33 | 0.33 | 0.33

## Slide 4: Developing Energy Projects
Chart: 
| Plug and Process Load | Mechanical Load | Lighting
Energy Use Categories | 0.33 | 0.33 | 0.33
Building Occupant Controlled:
Workplace Policy
Purchasing Guidelines
Education
Team Building - Competition
Plug Load Control Devices

## Slide 5: Success Story: Plug Load Occupancy Sensors
Received free from SCE
Installed on computer workstations
Savings – 60,000 kWh per year!

## Slide 6: Developing Energy Projects
Chart: 
| Plug and Process Load | Mechanical Load | Lighting
Energy Use Categories | 0.33 | 0.33 | 0.33
Energy Team Controlled:
Electronic Control Systems
High Efficiency
Innovation

## Slide 7
Los Baños Del Mar Pool Variable Speed Pumping
$15,500 annual savings
$22,882 Work Force Housing Grant
$11,620 SCE Rebate
Net Cost $2,700
Payback – 2 months
Replaced old equipment
  Maintenance Renewal
Success Story
Notes: Redo Los Banos

## Slide 8: Los Baños Del Mar Pool Condensing Boilers
Replaced 30 year old boilers
Saves 12,000 therms annually
Reduce gas use by 25%
$69,735 Investment
Funding SoCalGas
  On Bill Financing
  0% Interest
  10 Year Term
  $7,202 Incentive
Success Story

## Slide 9: Developing Energy Projects
Chart: 
| Plug and Process Load | Mechanical Load | Lighting
Energy Use Categories | 0.33 | 0.33 | 0.33
Chart: 
| Plug and Process Load | Mechanical Load | Lighting
Energy Use Categories | 0.33 | 0.33 | 0.33
Energy Team & User Controlled:
Controls – Adaptive Lighting
New Technologies - LED

## Slide 10
Granada Garage Lighting Improvements
Replaced Metal Halide with High Efficiency T-8 Fluorescent
$31,000 annual savings
1.7 year payback
$52,800 cost after rebate
Granada Garage Monthly Electrical Use
Before and After Lighting Improvements
Before
After
Success Story

## Slide 11: More Garage Lighting
Upgraded lighting in remaining 4 parking structures
$96,400 rebates
Net Cost - $121,271
$76,500 annual savings
Simple Payback – 1.8 Years
Reduces maintenance costs
Success Story

## Slide 12: LED Opportunities!
Offices
Outdoor Lighting
Street Lights
Parking Lots and Parking Structures

## Slide 13: LED Pool Light Retrofit
Cost - $11,706
$1,609 Incentive
Reduced Maintenance Costs
  Incandescent – 5,000 hours – 500 watts
  LED – 30,000 hours -70 watts
Better Light Quality
Saves 12,000 kWh and $2,318 Annually
BEFORE
AFTER
Success Story

## Slide 14: Lessons Learned
Sunk Cost Versus Personal Incentive
Negotiating the Arcane rules of the Utilities

## Slide 15: Sunk Cost Versus Personal Incentive
El Estero WWTP Fuel Cells – Installed 2005

## Slide 16: El Estero Wastewater Treatment Plant Fuel Cell Generation
Carbonyl Sulfide in the digester gas supply is keeping the fuel cells from running optimally.
Fuel Cells generate electricity and hot water for El Estero operations using digester gas for fuel. The fuel cell cogeneration system is operated under a Power Purchase Agreement (PPA), and required no capital investment by the City.
Notes: Redo

## Slide 17: Fuel Cell Power Production
The red line represents the potential system generation output
The orange curve represents the actual system generation output. Staff is exploring alternative generation technology to improve electricity production
Notes: REdo

## Slide 18: Fuel Cell Removal
On December 9, 2010 the fuel cells were removed to make room for engine cogeneration

## Slide 19: Engine Cogeneration

## Slide 20: El Estero Cogeneration PPA
650 kW generator
10-year contract
Provides free hot water
Provides most of the electrical needs of the plant
Produces over 4 million kWh per year

## Slide 21
Granada Garage Lighting Improvements
Completed in 2009
Replaced Metal Halide with High Efficiency T-8 Fluorescent
$31,000 annual savings
1.7 year payback
$52,800 cost after rebate
Granada Garage Monthly Electrical Use
Before and After Lighting Improvements
Before
After

## Slide 22: LED Opportunity “But we just did this!”
LED Lighting at Granada Garage
Net Cost - $125,521
Incentive - $9,717
Payback – 43 months
Cost to wait - $2,876 per month

## Slide 23: Arcane Rules of the Utilities
Affects:
  Incentive Programs
  Interconnection of Renewable Energy Generation Projects
  Ability to credit other accounts for excess energy production for Public Agencies – RES-BCT (AB 2466)
  Net Metering and Renewable Tariffs

## Slide 24: Arcane Rules of the Utilities Example: NEM and Renewable Tariffs
Stimulates Renewable Energy Markets
Net Metering – Provides for energy export and bill credits
Renewable Tariffs shift Time Related Demand to kWh (Demand to Energy)
Don’t start planning your project until you understand the Tariffs!

## Slide 25: Arcane Rules of the Utilities Example: NEM and Renewable Tariffs
Tariff | SCE Cap | Current | Available
Renewable (R) | 150 MW | 150 MW? | 0
SCE TOU8– A Option – Solar Only | 50 MW | 5.36 MW | 44.64 MW
NEM | 2,240 MW | 902.9 MW | 1337.1 MW
Tariff | Mid Peak kW | On Peak kW | Mid Peak kWh | On Peak kWh
TOU8-A | $0 | $0 | 10.4¢ | 33.1¢
TOU8-B | $7.11 | $25.16 | 6.7¢ | 12.7¢
SCE Summer Time of Use Costs
PG&E Has a Generation Demand Reduction – Ending in Dec. 31, 2016

## Slide 26: Options for annual net energy generation
NEM:
  Do nothing – lose your excess generation $
  Sell back to utility - > 4 cents/kWh
  Roll over balance to subsequent year
Government – Renewable Energy Self Generation Bill Credit Transfer (RES-BCT)
  AB 2466 (Laird, 2008)
  Transfers excess generation to Government or Campus TOU electrical account monthly

## Slide 27: RES-BCT Caveats
Limited by CSI Incentive Rules
  Power generated and used on premises
Standby Charges Apply
Possible Departing Load Charges
Cannot use “R” or “A” type tariffs for Generating Account
Apply for Rule 21 Export Interconnect Agreement
Extra monthly fees
Application fees

## Slide 28: Lessons Learned Summary
Don’t let Personal Incentives limit opportunities
Before you begin planning a conservation or renewable energy project:
  Work closely with your Utility Account Representative
  Educate Yourself

## Slide 29: Questions?